STM32 PLC
# Introduction
# How to use
# How to build PCB
# How to flash microcontroller
# How the C code works
# Available control programs
## PI Control – Control program 1
There are 3 PI inside STM32 PLC. PI controller is a proportional and integral controller with the algorithm.
Algorithm start:
1: E = SETPOINT – INPUT
2: I = I + G•E
3: PWM = P•E + I
4: ANALOG_OUTPUT = (P•E + I)/16
4: IF (ANTI-WINDUP == 1 AND E <= 0)
5:	I = 0
Algorithm end:
Where:
- E = The error between SETPOINT and INPUT
- I = The integral sum
- G = The integral gain
- PWM = Output signal for PWM
- ANALOG_OUTPUT = 0-20mA output. Division with 16 is for mapping 16-bit to 12-bit
- P = Proportional gain
- SETPOINT = The reference
Anti-winup is when integral I works as a proportional gain when INPUT >= SETPOINT. Anti-winup enables with high signal on digital inputs.
Controller	INPUT	OUTPUT	SETPOINT	P	G	ANTI_WINUP
1	ADC0	PWM0/AO0	Software	Software	Software	Software
2	ADC1	PWM1/AO1	Software	Software	Software	Software
3	ADC2	PWM2/AO2	Software	Software	Software	Software

## Pulse Count – Control program 2
There are 4 Pulse counter inside STM32 PLC. These pulse counters can be used for counting pulses. High and low are levels when the PWM output should be 0% or 100%.
Algorithm start:
1: IF (INPUT >= HIGH)
2:	OUTPUT = 0%
3:	PULSES = PULSES + 1
4: IF (INPUT <= LOW OR START == 1)
5:	OUTPUT = 100%
Algorithm end:
Where:
- INPUT = Measurement
- HIGH = Threshold measurement max level
- LOW = Threshold measurement min level
- OUTPUT = Pulse Width Modulation, in this case, its either ON or OFF
- PULSES = The counted pulses
- START = Digital input start
Counter	INPUT	OUTPUT	START	HIGH	LOW	PULSES
1	ADC0	PWM0	DI1	Software	Software	Saved at SD card
2	ADC1	PWM1	DI2	Software	Software	Saved at SD card
3	ADC2	PWM2	DI3	Software	Software	Saved at SD card
4	ADC3	PWM3	DI3	Software	Software	Saved at SD card

## MRAC Control – Control program 3
There are 3 MRAC inside STM32 PLC. MRAC controller is an adaptive PI controller with the algorithm based on MIT-rule. In other words, P-gain is just an integral too.
Algorithm start:
1: E = SETPOINT – INPUT
2: I1 = I1 – G•SETPOINT•E
3: I2 = I2 + G•INPUT•E
4: OUTPUT = SETPOINT•I1 – INPUT•I2
Algorithm end:
Where:
- E = The error between SETPOINT and INPUT
- I1 = The integral sum of the SETPOINT
- I2 = The integral sum of the output
- G = The integral gain
- OUTPUT = Output signal for PWM and analog output
- SETPOINT = The setpoint
Controller	INPUT	OUTPUT	SETPOINT	G
1	ADC0	PWM0/AO0	Software	Software
2	ADC1	PWM1/AO1	Software	Software
3	ADC2	PWM2/AO2	Software	Software

## ON/OFF Control – Control Program 4
There are 4 ON/OFF controller inside STM32 PLC.
Algorithm start:
1: IF (INPUT >= HIGH)
2:	OUTPUT = 0%
3: ELSE
4:	OUTPUT = 100%
Algorithm end:
Where:
- INPUT = Measurement
- HIGH = Threshold measurement max level
- OUTPUT = Pulse Width Modulation, in this case, its either ON or OFF
Counter	Y	OUTPUT	HIGH
1	ADC0	PWM0	Software
2	ADC1	PWM1	Software
3	ADC2	PWM2	Software
4	ADC3	PWM3	Software

## Input and Output PWM – Control program 5
This translates 4 analog inputs into 8 PWM outputs, or 4 analog inputs to 4 PWM outputs if single operation 0 to 100% is enabled.
Algorithm start:
1: IF (SINGLE_OPERATION == 1)
2:	OUTPUT_X = INPUT
3: ELSE
4:	OUTPUT_X = 50% - INPUT/2
5:	OUTPUT_Y = 50% + INPUT/2
Algorithm end:
Converter	INPUT	OUTPUT_X	OUTPUT_Y	SINGLE_OPERATION
1	ADC0	PWM0	PWM1	DI1
2	ADC1	PWM2	PWM3	DI2
3	ADC2	PWM4	PWM5	DI3
4	ADC3	PWM6	PWM7	DI4

## Input and Output Analog – Control program 6
This translates 3 analog inputs into 3 analog outputs.
Algorithm start:
1:	OUTPUT = INPUT/8
Algorithm end:
Converter	INPUT	OUTPUT
1	ADC0	AO0
2	ADC1	AO1
3	ADC2	AO2

## Digital output alarm – Control program 7
There are two alarms inside the STM32 PLC. Alarm A who enables the alarm on week day: d – hh:mm. Alarm B who enables the alarm on date: dd – hh:mm.
Where:
- d = Week day between 1 and 7
- hh = Hour between 0 and 23
- mm = Minute between 0 and 59
- dd = Date between 1 and 31
The alarm is active when date/weekday and clock hour is equal too the alarm and clock minute >= minute. Else not active. So enable the alarm at week day 7 (Sunday) and hour 8 and minute 30, then the alarm will be active at 30 minutes too 9 o’clock.
Algorithm start:
1: IF(ALARM_A_ACTIVE == 1)
2:	PWM0 = 100%
3:	PWM1 = 0%
4: ELSE
5:	PWM0 = 0%
6:	PWM1 = 100%
7: IF(ALARM_B_ACTIVE == 1)
8:	PWM2 = 100%
9:	PWM3 = 0%
10: ELSE
11:	PMW2 = 0%
12:	PWM3 = 100%
Algorithm end:
Converter	INPUT	OUTPUT
1	ADC0	AO0
2	ADC1	AO1
3	ADC2	AO2

# Auxiliary Valve Command – Control program 8
There are 4 Auxiliary Valve Commands inside STM32 PLC. Auxiliary Valve Command is included in ISO 11783-7 and SAE J1939 standard.
Algorithm start:
1: STANDARD_FLOW = INPUT/131
2: IF(VALVE_STATE == 1)
3:	VALVE = FOWARD
4: ELSE
5:	VALVE = BACKWARD
Algorithm end:
Valve	INPUT	VALVE_STATE
1	ADC0	DI1
2	ADC1	DI2
3	ADC2	DI3
4	ADC3	DI4

# Auxiliary Valve Command – Control program 8
There are 4 Auxiliary Valve Commands inside STM32 PLC. Auxiliary Valve Command is included in ISO 11783-7 and SAE J1939 standard.
Algorithm start:
1: STANDARD_FLOW = INPUT/131
2: IF(VALVE_STATE == 1)
3:	VALVE = FORWARD
4: ELSE
5:	VALVE = BACKWARD
Algorithm end:
Valve	INPUT	VALVE_STATE
1	ADC0	DI1
2	ADC1	DI2
3	ADC2	DI3
4	ADC3	DI4

# General Purpose Valve Command – Control program 9
There is a General Purpose Valve Commands inside STM32 PLC. General Purpose Valve Command is included in ISO 11783-7 and SAE J1939 standard.
Algorithm start:
1: EXTENDED_FLOW = INPUT
2: IF(VALVE_STATE == 1)
3:	VALVE = FORWARD
4: ELSE
5:	VALVE = BACKWARD
Algorithm end:
Valve	INPUT	VALVE_STATE	DESTINATION_ADDRESS
1	ADC0	DI1	Software